## PROJECT DESCRIPTION AND

REQUEST FOR ARCHITECTURAL/ENGINEERING SERVICES

HEATING PLANT AND BOILER UPGRADES #13D2C

Wisconsin Veterans Home – King

King

May 2013

# The Wisconsin Department of Veterans Affairs is requesting the selection of an Architect/Engineer to provide full design and construction administration services for the Heating Plant and Boiler Upgrades at the Wisconsin Veterans Home – King.

- Project Scope

- Project Description

This project will design and construct the Heating Plant and Boiler Upgrades project which includes replacement of burners on boilers 1 and 2, replacement of boiler 3 with a smaller boiler,  add an emergency generator, makeup air handling unit, , , new condensate tank and pumps, increased RO feedwater capacity, removal of coal handling equipment,  repair or demolish the existing smoke stack, upgrade to PLC based controls, install compressed air and perform various heating plant repairs and upgrades. Also included is further review of boilers 1 and 2 tubes, drums and refractory and review of stack economizer feasibility.

##### Project Location

King, Wisconsin

Wisconsin Veterans Home – King

- Project Background and Existing Conditions

The Wisconsin Veterans Home – King (Home) is a 721-bed campus serving the long term nursing care needs of veterans and their eligible dependents in 4 skilled nursing care buildings and support facilities. Building #403 is the Home’s central heating and cooling plant. The building houses three ca. 1951 boilers, two chillers, controls, piping and wiring associated with these functions, a 350Kw generator, maintenance space and abandoned coal bunkers. Steam provides energy for campus building heat, hot water, food preparation, humidification and various process purposes. Sixteen buildings, including the Home’s 4 skilled nursing care buildings are dependent on the trouble free operation of the heating and cooling plant.

The heating plant was constructed in 1951. The 3-20,000 lb. per hour (lb/h) saturated steam boilers operate at 60 PSI and were converted from coal to natural gas/fuel oil in 1973. At the time of their conversion, the useful life of the boiler’s water tubes, drums and settings were estimated at 10 to 20 years.  New single loop boiler operating controls were installed in 2002 and will be replaced with PLC controls. Boilers #’s 1 and 2 handle the campus winter heat, water heating and process loads. The fire boxes are solid and only in need of minor patching. Due to their age, these two boilers are in need of new burners, linkageless controls, air atomization and fan units.

The summer steam load which is primarily the kitchen and laundry processes peaks at 8,000 lb/h is handled by boiler #3.  The boiler is operating at less than optimal capacity and this load can be handled by a smaller, 15,000 lb/h boiler with a 10:1 turndown and greater efficiency. Cracked and loose fire bricks in the fire box will be repaired at a minimal cost in FY2013 to keep the boiler sound until its removal and replacement.

The 150’ brick smoke stack was lined with Gunnite back in the 1980’s. Its exterior only was inspected in 2000. An interior inspection of the smoke stack will take place in the spring of 2013 to determine its soundness and make a determination as to whether the smoke stack should be repaired or replaced with several smaller ones as part of this project.

This project includes the removal of main floor coal bunker equipment dating back to 1951.

Access to the cooling tower for maintenance will be made safer by the addition of a catwalk from the second floor to the cooling tower.

The existing 350kW generator currently provides emergency power to the heating plant, MacArthur Hall Freight Elevator, Security Building, a portion of Central Services, and Burns Clemens Hall.  A new 350 kW generator, complete with a 400kva transformer, transfer switches and feeds to Marden and Security Bldg., will provide the emergency power to all of the buildings listed above with the exception of Central Services. Included is review of generator location options. The existing 350 kW will then be solely used for the Central Services laundry and kitchen. At this time only a small portion of Central Services can operate during a power outage. This change will make all operations continuous during a power outage.

The old, undersized generator in the Marden Activity Center was damaged beyond repair during a thunderstorm several years ago. Current code prohibits the installation of a new generator in the same location, therefore power will come from the heating plant. Continuous power to the Marden Activity Center elevator is critical as the facility is dedicated to the resident activities. Life Safety is a concern as without emergency power during a power outage the elevator is inoperable, stopping at any point, even between floors, potentially stranding residents and staff.

Additional minor heating plant upgrades are included to improve efficiency of the facility.

A Heating Plant and Boiler Upgrades Study was conducted by GO/A Architects, Inc. and Grumman/Butkas, Associates dated September 15, 2012. The study developed the scope of work and project budget.

- Proposed Timetable

| A/E Advertisement | April 2013 |
| --- | --- |
| A/E Selection | May 2013 |
| Design Report to Building Commission | January 2014 |
| Bid Opening | May 2014 |
| Construction Begins | July 2014 |
| Substantial Completion | October 2015 |

- Proposed Budget

| Construction | $ |
| --- | --- |
| Contingency |  |
| Architect/Engineer & Environmental Permitting |  |
| DFD Fees |  |
| Equipment |  |
| Total Project Budget | $1,936,000 |

# Agency Contact: Susan Mattix, 608-264-6093, susan.mattix@dva.wisconsin.gov

# AE Scope of Services

The AE will meet the requirements of the DFD AE Policy and Procedure Manual.